## Punch Sheet
FSO/Project Name :
iCenter Sales Order No : |  |  |  |  | Cabinet ID:
Sr.No | Refference No. | Punch/Action Point Description | Category | Inspected by |  | Implemented By(Production) |  | Checked by
|  |  |  | Initials | Date | Intials | Date | Intials | Date

## Sheet1 (2) (hidden)
Column1 | Column2 | Column3 | Column4 | Column5 | Column6 | Column7 | Column8 | Column9 | Column10 | Ref Key
#REF!
FSO/Project Name : |  | QG NFS | [7 empty] | #REF!
#REF!
iCenter Sales Order No : |  | 2000710 |  |  | Cabinet ID: |  | SJBC-381A0026 |  |  | #REF!
#REF!
#REF!
Sr.No | Refference No. | Punch/Action Point Description | Category | Inspected by |  | Implemented By(Production) |  | Checked by |  | #REF!
|  |  |  | Initials | Date | Intials | Date | Intials | Date | #REF!
1 | 0 | X1-2,4 Wire missing | Incomplete wiring | Prathamesh | 45975 |  |  |  |  | #REF!
2 | 0 | FBS2-10 Shortink are missing Front and rear | Incomplete Asembly | Prathamesh | 45975 |  |  |  |  | #REF!
3 | 0 | X4-2,4 Wire connection wrong | Wrong Wiring | Prathamesh | 45975 |  |  |  |  | #REF!
4 | 0 | X8 TB Group terminal marker missing | Incomplete Asembly | Prathamesh | 45975 |  |  |  |  | #REF!
5 | 0 | UIRJD03-CIOC03,CIOC04 Supply wire not properly inserted | Workmanship error | Prathamesh | 45975 |  |  |  |  | #REF!
6 | 0 | X10-2 wire connection wrong | Wrong Wiring | Prathamesh | 45975 |  |  |  |  | #REF!
7 | 0 | IE2 Bar / SB6 earthing wire sleeve not properly installed | Workmanship error | Prathamesh | 45975 |  |  |  |  | #REF!
8 | 0 | XALM-1,6 ferrule wrong both side (output) | Workmanship error | Prathamesh | 45975 |  |  |  |  | #REF!
9 | 0 | CR13,CR14 Wire connection interchanged | Workmanship error | Prathamesh | 45975 |  |  |  |  | #REF!
10 | 0 | Network cable missing with tag ferrule | Material Shortfall | Prathamesh | 45975 |  |  |  |  | #REF!
11 | 0 | [8 empty] | #REF!
12 | 0 | [8 empty] | #REF!
| 0 | [8 empty] | #REF!
| 0 | [8 empty] | #REF!
| 0 | [8 empty] | #REF!
| 0 | [8 empty] | #REF!
| 0 | [8 empty] | #REF!
| 0 | [8 empty] | #REF!
| 0 | [8 empty] | #REF!
| 0 | [8 empty] | #REF!
| 0 | [8 empty] | #REF!
| 0 | [8 empty] | #REF!
| 0 | [8 empty] | #REF!
| 0 | [8 empty] | #REF!
| 0 | [8 empty] | #REF!
| 0 | [8 empty] | #REF!
| 0 | [8 empty] | #REF!
| 0 | [8 empty] | #REF!
| 0 | [8 empty] | #REF!
| 0 | [8 empty] | #REF!
| 0 | [8 empty] | #REF!
| 0 | [8 empty] | #REF!
| 0 | [8 empty] | #REF!
| 0 | [8 empty] | #REF!
| 0 | [8 empty] | #REF!
| 0 | [8 empty] | #REF!
| 0 | [8 empty] | #REF!
| 0 | [8 empty] | #REF!
| 0 | [8 empty] | #REF!
| 0 | [8 empty] | #REF!
| 0 | [8 empty] | #REF!
| 0 | [8 empty] | #REF!
| 0 | [8 empty] | #REF!
| 0 | [8 empty] | #REF!
| 0 | [8 empty] | #REF!
| 0 | [8 empty] | #REF!
| 0 | [8 empty] | #REF!
| 0 | [8 empty] | #REF!
| 0 | [8 empty] | #REF!
| 0 | [8 empty] | #REF!
| 0 | [8 empty] | #REF!
| 0 | [8 empty] | #REF!
| 0 | [8 empty] | #REF!
| 0 | [8 empty] | #REF!
| 0 | [8 empty] | #REF!
| 0 | [8 empty] | #REF!
| 0 | [8 empty] | #REF!
| 0 | [8 empty] | #REF!
| 0 | [8 empty] | #REF!
| 0 | [8 empty] | #REF!
| 0 | [8 empty] | #REF!
| 0 | [8 empty] | #REF!
| 0 | [8 empty] | #REF!
| 0 | [8 empty] | #REF!
| 0 | [8 empty] | #REF!
| 0 | [8 empty] | #REF!
| 0 | [8 empty] | #REF!
| 0 | [8 empty] | #REF!
| 0 | [8 empty] | #REF!
| 0 | [8 empty] | #REF!
| 0 | [8 empty] | #REF!
| 0 | [8 empty] | #REF!
| 0 | [8 empty] | #REF!
| 0 | [8 empty] | #REF!
| 0 | [8 empty] | #REF!
| 0 | [8 empty] | #REF!
| 0 | [8 empty] | #REF!
| 0 | [8 empty] | #REF!
| 0 | [8 empty] | #REF!
| 0 | [8 empty] | #REF!
| 0 | [8 empty] | #REF!
| 0 | [8 empty] | #REF!
| 0 | [8 empty] | #REF!
| 0 | [8 empty] | #REF!
| 0 | [8 empty] | #REF!
| 0 | [8 empty] | #REF!
| 0 | [8 empty] | #REF!
| 0 | [8 empty] | #REF!
| 0 | [8 empty] | #REF!
| 0 | [8 empty] | #REF!
| 0 | [8 empty] | #REF!
| 0 | [8 empty] | #REF!
| 0 | [8 empty] | #REF!
| 0 | [8 empty] | #REF!
| 0 | [8 empty] | #REF!
| 0 | [8 empty] | #REF!
| 0 | [8 empty] | #REF!
| 0 | [8 empty] | #REF!
| 0 | [8 empty] | #REF!
| 0 | [8 empty] | #REF!
| 0 | [8 empty] | #REF!
| 0 | [8 empty] | #REF!
| 0 | [8 empty] | #REF!
| 0 | [8 empty] | #REF!
| 0 | [8 empty] | #REF!
| 0 | [8 empty] | #REF!
| 0 | [8 empty] | #REF!
| 0 | [8 empty] | #REF!
| 0 | [8 empty] | #REF!
| 0 | [8 empty] | #REF!
| 0 | [8 empty] | #REF!
| 0 | [8 empty] | #REF!
| 0 | [8 empty] | #REF!
| 0 | [8 empty] | #REF!
| 0 | [8 empty] | #REF!
| 0 | [8 empty] | #REF!
| 0 | [8 empty] | #REF!
| 0 | [8 empty] | #REF!
| 0 | [8 empty] | #REF!
| 0 | [8 empty] | #REF!
| 0 | [8 empty] | #REF!
| 0 | [8 empty] | #REF!
| 0 | [8 empty] | #REF!
| 0 | [8 empty] | #REF!
| 0 | [8 empty] | #REF!
| 0 | [8 empty] | #REF!
| 0 | [8 empty] | #REF!
| 0 | [8 empty] | #REF!
| 0 | [8 empty] | #REF!
| 0 | [8 empty] | #REF!
| 0 | [8 empty] | #REF!
| 0 | [8 empty] | #REF!
| 0 | [8 empty] | #REF!
| 0 | [8 empty] | #REF!
| 0 | [8 empty] | #REF!
| 0 | [8 empty] | #REF!
| 0 | [8 empty] | #REF!
| 0 | [8 empty] | #REF!
| 0 | [8 empty] | #REF!
| 0 | [8 empty] | #REF!
| 0 | [8 empty] | #REF!
| 0 | [8 empty] | #REF!
| 0 | [8 empty] | #REF!
| 0 | [8 empty] | #REF!
| 0 | [8 empty] | #REF!
| 0 | [8 empty] | #REF!
| 0 | [8 empty] | #REF!
| 0 | [8 empty] | #REF!
| 0 | [8 empty] | #REF!
| 0 | [8 empty] | #REF!
| 0 | [8 empty] | #REF!
| 0 | [8 empty] | #REF!
| 0 | [8 empty] | #REF!

## Interphase
FSO/Project Name:
iCenter Sales Order No: |  |  | Cabinet ID:
| Refference No. | Checklist | Status | Test Performed by: Name/Signature | Date | Remarks
PROJECT INFO SHEET | 1 | Check that the first page in Book "Project Info Sheet" is correct. |  |  |  |  | 1
| 2 | Check for the engineer’s signature on the first page, all the changes he made on the drawings, and on the old version sheets. |  |  |  |  | 2
MECHANICAL ASSEMBLY | 3 | Mounting plate checking:- not scratched/properly fixed with the hardware and gasket on the cutout |  |  |  |  | 3
| 4 | Door checking:- Cut out, Hinges, Gasket Door handle lock as per drg |  |  |  |  | 4
| 5 | Side panel checking: any scratches or paint peel off or properly install. |  |  |  |  | 5
| 6 | Visual check for any scratches, damage, chroming or painting problems, etc. at the cabinet. |  |  |  |  | 6
| 7 | Cable ducts:- Mounting and checking the cable ducts according to the drawing (dimensions; color etc) / not to be any scratches on them / to be at the correct dimension / to be cut straight. |  |  |  |  | 7
| 8 | DIN Rails:- Checking and correct mounting / fixed with the appropriate screws. They have to be fixed accordingly. |  |  |  |  | 8
| 9 | Plinth: Checking for the plinth to cabinet fixing hardware with the correct length in case of AVP (M10*40) |  |  |  |  | 9
COMPONENT ASSEMBLY | 10 | Components: Check that all the components are there and the quantity is the same as per the drawing / BOM. |  |  |  |  | 10
| 11 | Component assembly: the components are mounted according to the main drawing / visual check (not to be damaged) / terminals and components fixed appropriately. |  |  |  |  | 11
| 12 | Labelling & Ferrule:- Check that the labels match the label type on Project Info Sheet. |  |  |  |  | 12
| 13 | Ferrule:- Check the direction of the writing /the fonts need to be the same/grounding ferrules at every wire/damage/ wrong/properly heat shrinked. |  |  |  |  | 13
| 14 | Power wiring:- connections executed correctly / the wire color /wire size/ crimped properly / free wires need to be isolated. |  |  |  |  | 14
| 15 | I/O wiring:- connections executed correctly / the wire color /wire size/ crimped properly / free wires need to be isolated. |  |  |  |  | 15
| 16 | Grounding needs to be according to the drawing/standard. Grounding label for every wire. Check that the grounding screws and grounding rules are followed |  |  |  |  | 16
| 17 | Check that the fuses and MCB are according to the drawing. |  |  |  |  | 17
| 18 | Check the wire position in the cable ducts, AC, DC, etc. |  |  |  |  | 18
FINAL ASSEMBLY | 19 | Check that all components are identified with the label required in the drawing and they are consistent (written identically / not damaged etc). Check the label fixed on AC ducts. |  |  |  |  | 19
| 20 | Verify the wire routing inside the ducts and ensure that there are no joints |  |  |  |  | 20
| 21 | Check that the labels are according to the specifications on the drawing. |  |  |  |  | 21
| 22 | Wiring dressing/cable tie cutting |  |  |  |  | 22
| 23 | Check whether the duct cover is fixed or not |  |  |  |  | 23
| 24 | Check the cleanliness of the cabinet. |  |  |  |  | 24
| 25 | Check that all the screws are fixed tight. |  |  |  |  | 25
| 26 | Check Ex Label Plate and Instruction Plate |  |  |  |  | 26
DOCUMENTATION | 27 | Check that the system assembly checklist and Traveller system are signed by the Assembler/technicians. |  |  |  |  | 27
| 28 | Check that the connections are signed on the drawings. |  |  |  |  | 28
| 29 | Check that the assembly table with equipment used is entered in the equipment and discrepancy record. |  |  |  |  | 29
| 30 | If there are missing parts in the cabinet check that they are listed in the discrepancy record form |  |  |  |  | 30
| 31 | Check for the CE mark, if required. |  |  |  |  | 31